## KANAODON
REHABILITATION AND IMPROVEMENT OF KANAODON WATER PROJECT IN TURKANA COUNTY
Notes: The contractor is reminded to visit the site before filling the respective rates in the bills of quantities and to ascertain the extent of the conditions of site. All quantified works in the tender are provisional and inclusive of VAT.The contractor shall provide, erect and maintain all safety measures requirements according to specifications. All materials must be approved by IRC engineer before they are used in construction.
ITEM | DESCRIPTION | Unit | Qty | Rate (Inclusive of Vat and any other duties/taxes) KES | Amnt (KES)
1 | PRELIMINARIES AND GENERAL ITEMS
1.01 | Mobilization and demobilization from site about 50km from Lokichar town to project site | LS | 1
1.02 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
Sub-Total
2 | DISMANTLING OF HAND PUMNP & INSTALLATION OF SOLAR POWERED SYSTEM
Dismantling of Hand Pump and Borehole inspection
2.01 | Allow for removal of hand pump and its accessories | LS | 1
Pump Intallation
2.02 | Supply, install and test 1.5" High Density Dayliff uPVC riser pipes (PN12) and accessories to connect to the submersible pump | m | 42
2.03 | Supply and install 25mm uPVC class D airline pipes | m | 42
2.04 | Supply, install and test a submersible pump(SQF 5-70 Grundfos Pump or equivalent and as directed by the client capable of producing 5.2m³/hr at a total head of 56.8 m) complete with motor, solar PV Disconnect, controller to match the the pump motor rating and all installation sundries or as per the results obtained during the inspection. | No. | 1
Supply and Installation of Solar PV System
2.05 | Supply all materials, erect solar panels support structure - 4m high and supported by 50mm x 50mm x 4mm HS beams (panels to be permanently fixed on 50mmx50mmx3mm angle lines using steel bolts), designed to BS5950. | LS | 1
2.06 | Supply, install and connect 8 No. 400W Jinko solar or Equivalent Monocrystalline modules on the solar array stand in 2.05 above capable of providing power commensurate to the pump in 2.04 above complete with solar pumping inverter, PV surge protection device PV protect 1000-125, well probe sensor, Delta solar lighting arrestor DC-LA302DC. Cost to include for all other associated accessories and commissioning of the works | LS | 1
2.07 | Provide and connect for power cables (sized to power rating) with cable end terminals for connection from solar power source to switch gear up to borehole pump, cost to include all accessories. Pump cable length estimated at 60 m. | Ls | 1
Supply, handle, deliver to site, lay and joint the following
2.08 | 1 1/2" GI sweep bend | NO | 1
2.09 | 1 1/2" GI socket | NO | 1
2.1 | 1 1/2" 400mm long threaded GI pipe | NO | 1
2.11 | 1 1/2" dia Non Return Valve | NO | 1
2.12 | 1 1/2" dia Gate valve | NO | 1
2.13 | 1 1/2" GI union | NO | 1
2.14 | 1 1/2" Water Meter (Woltmann Type or its equivalent) | NO | 1
2.15 | 1 1/2" GI elbow | NO | 2
2.16 | 1 1/2" hexagonal GI nipple | NO | 2
Sub-Total
3 | BOREHOLE PROTECTION (CONSTRUCTION OF BOREHOLE CHABER - 3.2M X 3.2M)
3.01 | Excavate starting from ground level a 600mm wide foundation trench to a depth not exceeding 1.5m in normal soil | CUM | 24
3.02 | Allow for plunking and strutting sides of excavation trenches | Ls | 1
Fillings
3.03 | Return, fill and ram around foundations | CUM | 16.8
Footing
3.02 | Supply all materials and cast a 50mm thick concrete blinding for foundation footing (mix ratio 1:4:8) | SM | 10
3.03 | Supply and fix steel bars in foundation trench including cutting, bending, hoisting, and tying wire and supporting all in position, D12 @ 200 c/c | KG | 220
3.04 | Supply all materials and cast a 200mm thick vibrated reinforced foundation concrete 1:2:4 (concrete class 20/20) | CUM | 1.7
Walling
3.05 | Supply and fix steel bars including cutting, bending, hoisting, and tying wire and supporting all in position, D10 @ 200 c/c | KG | 312
Formwork;
3.06 | Sides of the walling | SM | 36
3.07 | Supply all materials and cast a 200mm wide vibrated reinforced walling 1:2:4 (concrete class 20/20) | CUM | 7
Slab
3.08 | Supply and fix steel bars including cutting, bending, hoisting, and tying wire and supporting all in position, D10 @ 200 c/c | KG | 188
Formwork;
3.09 | Sides of the slab | SM | 3
3.1 | Supply all materials and cast a 150mm thick vibrated reinforced slab 1:2:4 (concrete class 20/20) | CUM | 1.8
Access cover
3.11 | Fabricate and fix access cover overal size 750x750mm made of 3mm thick chequered plate fixed to angle line framing with heavy duty bushes. Cost to include provision of closing system. | NO | 1
Sub-Total
4 | TANK PLATFPORM (3MX3M), TANK AND STAND PIPE
0
4.01 | Excavate trench for Pipes minimum depth of 400mm and backfill as directed by the Engineer. | M | 60
4.02 | Clear site of all bushes, grass, scrubs and roots. | SM | 7
4.03 | Excavate over site to remove top vegetation soil 200mm and dispose away from site as instructed by the Engineer | SM | 7
The contractor is reminded that all concrete works must be vibrated using a poker vibrator and all scheduling, dimensioning, bending and cutting of steel reinforcement for concrete to be as per BS 4466
4.04 | Excavate starting from stripped level a 600mm wide foundation trench to a depth not exceeding 0.5m in normal soil | CUM | 5
Fillings
4.05 | Return, fill and ram around foundations | CUM | 2
Mass Concrete
4.06 | Supply all materials and cast a 50mm thick concrete blinding to bed of foundation wall (mix ratio 1:4:8) | SM | 6
4.07 | Supply and fix steel bars in foundation trench concrete work including cutting, bending, hoisting, and tying wire and supporting all in position, D12 @ 200 c/c | KG | 45
Reinforced concrete
4.08 | Supply all materials and cast a 150mm thick vibrated reinforced foundation concrete 1:2:4 (concrete class 20/20) | CUM | 1
Rough natural stone with crushing strength 12Kn
4.09 | Supply and build, 200mm thick stone foundation walling in cement and sand mortar (1:3). Reinforce with and including 20swg x 25mm wide hoop iron in every alternative course; height 1.2m. | SM | 20
4.1 | 300mm thick approved hard-core,well compacted in layers not exceeding 150mm and blinded using 50mm marram/quarry dust | CM | 12
4.11 | Rough formwork to sides of slab | SM | 12
4.12 | Supply and fix steel bars in slab concrete work including cutting, bending, hoisting, and tying wire and supporting all in position, D8 @ 200 c/c | KG | 50
4.13 | Supply all materials and cast a 175mm vibrated reinforced concrete slab mix1:2:4 or class 20/20 | CUM | 2
4.14 | 15mm thick two coat cement sand (1:3) plaster trowelled smooth and comprising 12mm backing and 3mm finishing coat the columns. | SM | 30
4.15 | Provisional sum for plumbing works including chasing, installing sleeves in concrete, excavation threading, portable power supply and making good all damaged areas | LS | 1
4.16 | Supply and install a plastic water storage tank 10m³ Kentainer type or equivalent to be approved by engineer, drilled with inlet(65mm), outlet(65mm) and overflow(65mm) holes and necessary flanges fittings | No | 1
Supply, handle, deliver to site, lay and joint the following
4.17 | 50mmx1 1/2'' HDPE Adaptor | NO | 2
4.18 | 50mm dia HDPE PN12.5 Pipe | LM | 50
4.19 | 1 1/2" GI elbow | NO | 4
4.2 | 1 1/2" dia Gate valve | NO | 2
4.21 | 1 1/2" GI union | NO | 2
4.22 | 1 1/2" hexagonal GI nipple | NO | 4
4.23 | 1 1/2" 3000mm long threaded GI pipe | NO | 1
4.24 | 1 1/2" 1500mm long threaded GI pipe | NO | 1
4.25 | Block Boards | PC | 9
4.26 | 1 1/2" long threaded GI nipple | NO | 2
4.27 | 1 1/2" backnuts | NO | 6
TAPSTAND
4.28 | Erect 1 No. stand pipe at the end 6m from the tank as directed by Engineer Note: The stand pipe will consist of 1" GS stand pipe, ¾" pegler tap, 1" pegler Gate Valve, 1" union, 11/4"x1" R. Bush 1" GI elbows (2No.) Concrete stand pipe support and slab | No. | 1
Soak Away Pit
4.29 | Bulk excavations 2m diameter x 3.0m depth hole | CUM | 10 |  | 0
4.3 | Hardcore filling to 2.7m depth | CUM | 8 |  | 0
4.31 | Supply and lay 500 gauge polythene damp proof membrane over the hardcore surface | SM | 4 |  | 0
4.32 | 300mm thick normal soil backfilled in 2 layers of 150mm each and well compacted | SM | 4 |  | 0
4.33 | Supply and fix 4" dia gully trap | NO | 1 |  | 0
4.34 | Supply and fix 4" dia waste pipe | M | 3 |  | 0
4.35 | Supply and fix 4" dia Swept Bend With Inspection | NO | 2 |  | 0
| Sub-Total |  |  |  | 0
5 | CHLORINE DOSING UNIT
5.01 | Supply and install klorman inline chlorinator and supply 3 extra catridges to allow for 6 months of supply. | No | 1
| Sub-Total |  |  |  | 0
6 | CATTLE TROUGH (1NO)
Cattle trough 10m long and located n.e 30m from the community water point as designed to detail with all plumbing works from the community water point incorporating a 30m long HDPE Pipe PN10 with all fittings to trough. Include for 75 mm thick concrete slab for manhole cover as per attached drawing
6.01 | Excavate trench for Pipes minimum depth of 400mm and backfill as directed by the Engineer. | M | 60
6.02 | Clear and Excavate over site soil material to reduce levels not exceeding 225mm deep and cart away | SM | 20
6.03 | Excavation for raft foundation not exceeding 0.6m deep starting from the reduced level | SM | 20
6.04 | 300mm thick approved hard-core,well compacted in layers not exceeding 150mm and blinded using 50mm marram/quarry dust | SM | 20
6.05 | Plain concrete class 20 vibrated in foundation base 125mm thick on BRC A 142 | CM | 2.5
6.06 | Plain and place BRC A142 | SM | 20
6.06 | Approved local stone; squared and rough chisel dressed on one side,bedding and jointing in cement mortar (1:3) in walls 150mm thick.Provide for 1.5ft long 2" dia. GI pipe class A as scour with end cap. | SM | 9
6.07 | Plaster; 25mm with cement, Water proofing and sand mortar 1:1:3 mix internally and floor | SM | 10
6.08 | Plaster; 25mm with cement sand mortar 1:3 mix externally | SM | 9
6.09 | Provide 2.5m wide Stone pitched lining around the water trough | SM | 64
Supply, handle, deliver to site, lay and joint the following
6.1 | 50mmx 1 1/2'' HDPE Adaptor | NO | 2
6.11 | 50mm dia HDPE PN12.5 Pipe | LM | 60
6.12 | 1 1/2x1" Reducing socket | NO | 1
6.13 | 1" GI elbow | NO | 2
6.14 | 1" dia Gate valve | NO | 1
6.15 | 1" GI Pipe Threaded both sides of length 1m | NO | 1
6.16 | 1" GI union | NO | 1
6.17 | 1" hexagonal GI nipple | NO | 2
6.18 | Polythene sheet | PC | 9
6.19 | 1" Float Valve | NO | 1
| Sub-Total |  |  |  | 0
7 | FENCING
EXCAVATION
7.01 | Excavate starting from ground level a 300mm diameter pit to an average depth of 600mm (0.6m) at a distance of 3000mm centre to centre in normal soil including stays holes fixed at a distance of 20m centre to centre and at all corners | CM | 1.5 |  | 0
7.02 | Excavate 200x150mm trench a long the fence to receive chainlink ground achor concrete (ms) | CM | 1 |  | 0
7.03 | FENCING WORKS
7.04 | Supply all materials and cast 0.3m diameter x 0.6m depth concrete; concrete mix 1:3:6 class 15/20 and allow for curing of all concrete works | CM | 1.3 |  | 0
7.05 | Supply and fix in concrete foundation 3.0m high 50mm x 50mm x 4mm mild steel angles, top of the angle section cranked a distance of 300 and lower end with welded lugs including drilling 6 holes for straining wire and priming with red oxide primer before delivery to site. | NO | 16 |  | 0
7.06 | Ditto in 3above, but for strainer post at every corner and midpoint posts, both sides, but 1.5m long welded on to the post being supported. | NO | 14 |  | 0
7.07 | Supply and fix Gauge 12.5 chain link fence 2.4m high tied onto the 50mm x 50mm x 4mm angles(ms) adequately (at 6 points on the individual angle section) by binding wire. Cost should include cost of binding wire, cutting, tying and fixing. | LM | 40 |  | 0
7.08 | Supply and fix concrete mix 1:3:6 to 200x150mm deep trench and cast with the chain link. | CM | 1 |  | 0
| Supply and fix plain straining wire fixed through the 50mm x 50mm x 3mm mild steel angles standards- 3 lines | LM | 120 |  | 0
7.09 | Supply and fix plain barbed wire gauge 12.5 fixed through the 50mm x 50mm x 3mm mild steel angles standards- 6 lines | LM | 240 |  | 0
GATES
The contractor is reminded to include in his pricing, the cost of supply, cutting, waste and erecting and all other necessary fittings including welding lugs onto the angle bars etc. Steel sections and the necessary fixing and anchorage to be treated as described in the specifications. The gate concrete columns of 400 x 500mm; chainlink and barbed wire properly fixed onto the columns.
Excavations
7.1 | Excavate pits for gate columns commencing from ground level and not exceeding 1.5m deep. | CM | 3 |  | 0
7.11 | Concrete
7.12 | Vibrated Reinforced Concrete mix 1:2:4, mixed aggregates to:
7.13 | Column bases | CM | 1 |  | 0
7.14 | Columns | CM | 2 |  | 0
7.15 | Reinforcements
7.16 | High yield twisted Mild Steel bars to BS4449 including laps, bends, hooks, tie wires and spacer blocks in:-
7.17 | 16mm Diameter | KG | 58 |  | 0
7.18 | 12mm Diameter | KG | 15 |  | 0
7.19 | 8mm Diameter | KG | 11 |  | 0
Main gate and Pedestrian gate
| Purpose made mild steel gate overall size 4000 mm x 2100 mm high in two equal leaves fabricated from 50 mm x 50 mm x 4 mm thick SHS braces and framed all round 100x50x3mm thick RHS middle rails and 25 mm x 25 mm x 3 mm thick sections framing at 100mm centres and including all iron monger and accessories and 4no. 100x100x4mm thick gate posts fixed to column and applying one coat of red oxide primer before delivery to site. | NO | 1 |  | 0
7.2 | Ditto; 1200x2400mm pedestrian gate, single. | NO | 1 |  | 0
Finishes
7.21 | 15mm thick two coat cement sand (1:3) plaster trowelled smooth and comprising 12mm backing and 3mm finishing coat the columns. | SM | 13 |  | 0
7.22 | Prepare and apply three coats of gloss oil paint; 'Premium Grade brand' to column surfaces | SM | 13 |  | 0
7.23 | Prepare and apply under coat(red oxide) and two coats of gloss oil paint; 'Premium Grade brand (colour- to be defined by Client)' to column surfaces to the main gate doors and pedestrian gate | SM | 28 |  | 0
Formwork
7.24
| Sawn softwood formwork to the side columns | SM | 17 |  | 0
| Sub-Total |  |  |  | 0
GRAND SUMMARY PAGE
1 | PRELIMINARIES AND GENERAL ITEMS
2 | DISMANTLING OF HAND PUMNP & INSTALLATION OF SOLAR POWERED SYSTEM
3 | BOREHOLE PROTECTION (CONSTRUCTION OF BOREHOLE CHABER - 3.2M X 3.2M)
4 | TANK PLATFPORM (3MX3M), TANK AND STAND PIPE
5 | CHLORINE DOSING UNIT
6 | CATTLE TROUGH (1NO)
7 | FENCING
GRAND TOTAL