## HOST LOT 1
HOST SCHOOLS - LOT 1-Kakuma girls-Komudei-Nang'olemaret-Towokayeni
REHABILITATION AND IMPROVEMENT OF WATER SUPPLY AT KAKUMA GIRL'S PRIMARY SCHOOL
ITEM | DESCRIPTION | Unit | Qty | Rate (KSH) | Amnt (Ksh, Inclusive of VAT and Other duties
1 | Preliminary and general items
1.01 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
| Total |  |  |  | 0
2 | Rehabilitation of 2.5m Steel Tower and Tank
2.01 | Supply of 3" dia GI Class C 3000mm long | NO | 1
2.02 | Supply of 2" dia GI Class C 3000mm long | NO | 1
2.03 | Supply of 1 1/4" dia GI Class C 1500mm long | NO | 2
2.04 | Supply of 1" dia GI Class B 3000mm long | NO | 1
2.05 | Supply of 1" dia GI Class B 1000mm long | NO | 2
2.06 | Provide for mass concrete class 25 for middle support column. The column to be welded with 12mm dia steel dowel bars before concreting. | CM | 0.15
2.07 | Provide for welding of the above members as directed by the engineer | LS | 1
2.08 | Supply and install a plastic water storage tank 10m³ Kentainer type or equivalent to be approved by engineer, drilled with inlet(40mm), outlet(50mm) and overflow(50mm) holes and necessary flanges fittings | No | 1
Supply, handle, deliver to site, lay and joint the following
2.09 | 1 1/2" GI pipe | NO | 5
2.1 | 1 1/2" GI Socket | NO | 4
2.11 | 1 1/2" GI elbow | NO | 4
2.12 | 1 1/2" dia Gate valve | NO | 2
2.13 | 1 1/2" GI union | NO | 2
2.14 | 1 1/2" hexagonal GI nipple | NO | 4
2.15 | 1 1/2" 4000mm long threaded GI pipe | NO | 1
2.16 | 1 1/2" long threaded GI nipple | NO | 2
2.17 | 1 1/2" backnuts | NO | 4
Sub-Total
3 | Connection to bathroom
3.01 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 230m) from tank to water point | M | 90
3.02 | Supply and lay 50mm HDPE pipe PN12.5 | M | 90
3.03 | Allow for plumbing works for the 4 bathrooms including installation of GI shower roses. NOTE:Piping within the latrine to be PPR and all joints to be done using the appropriate tools | Item | 1
Sub-Total
4 | 1 No. Handwashing Point at the Latrine location
4.01 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 70m) from tank to water point | M | 70
4.02 | Excavation to level foundation base to receive hardcore filling | CM | 3.5
4.03 | Provide Place and compact approved hardcore to the thickness shown in the drawing.and ram to attain even level | SM | 11
4.04 | Blinding Concrete, 50 mm thick Class 15/20 to base of the Tapstand | SM | 11
4.05 | Formwork for platform | SM | 3
4.06 | Reinforced Concrete Class 20/20 to the floor Slab as directed by Engineer at site | CM | 1.2
4.07 | Provide BRC mesh class A142 to be placed at the floor slab as directed by Engineer at site | SM | 8
4.08 | 225 mm thick | SM | 1.2
Plastering
4.09 | Plaster; 25mm with cement, Water proofing and sand mortar 1:1:3 mix on vertical faces of the tapstand | SM | 3
Pipes and Fittings
4.1 | Supply and lay 40mm HDPE pipe PN12.5 | M | 70
4.11 | 40mm HDPE male Adaptor | NO | 3
4.12 | 1 1/4" GI pipe | NO | 1
4.13 | 1 1/4" x 1" Reducing GI Socket | NO | 1
4.14 | 1" GI Pipe Threaded both sides of length 2m | NO | 1
4.15 | 1" GI Pipe Threaded both sides of length 1m | NO | 1
4.16 | 1" GI Pipe Threaded both sides of length 400mm | NO | 2
4.17 | 1" dia GI elbows | NO | 2
4.18 | 1" dia equal GI tee | NO | 2
4.19 | 1" dia cross GI tee | NO | 1
4.2 | 1" dia Long Nipples | NO | 7
4.21 | 1" dia Hex Nipples | NO | 2
4.22 | 1/2" dia Hex Nipples | NO | 14
4.22 | 1" dia GI sockets | NO | 2
4.23 | 1" dia Union | NO | 1
4.24 | 1" dia peglar taps | NO | 6
4.25 | 1/2" dia peglar taps | NO | 14
Soak Away Pit
4.25 | Bulk excavations 2m diameter x 3.0m depth hole | CUM | 10
4.26 | Hardcore filling to 2.7m depth | CUM | 8
4.27 | Supply and lay 500 gauge polythene damp proof membrane over the hardcore surface | SM | 4
4.28 | 300mm thick normal soil backfilled in 2 layers of 150mm each and well compacted | SM | 4
4.29 | Construct 450x450x300mm deep silt trap including supply and installation of manhole cover | No. | 1
4.3 | Supply and fix 4" dia gully trap | NO | 1
4.31 | Supply and fix 4" dia waste pipe | M | 3
4.32 | Supply and fix 4" dia Swept Bend With Inspection | NO | 2
Sub-Total for HWS
GRAND SUMMARY PAGE
1 | Preliminary and general items
2 | Rehabilitation of 2.5m Steel Tower and Tank
3 | Connection to bathroom
4 | 1 No. Handwashing Point at the Latrine location
TOTAL
Add 10% for Contingencies
GRAND TOTAL
REHABILITATION AND IMPROVEMENT OF WATER SUPPLY AT KOMUDEI PRIMARY SCHOOL
ITEM | DESCRIPTION | Unit | Qty | Rate (KSH) | Amnt (Ksh) Inclusive of VAT and Other duties
1 | Preliminary and General items
1.01 | Mobilization of materials and personnel 140km from Lodwar Town to sites (Komudei, Towokayeni, Nang'olemaret and Kakuma Girls Primary Schools). Rate shall be inclusive of setting up site and temporary stores, demobilization after completion of works | LS | 1
1.02 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
Total
2 | Repair/Construction of Tank Platform (2.5mx5m)
2.01 | Clear site of all bushes, grass, scrubs and roots. | SM | 21
2.02 | Excavate over site to remove top vegetation soil 200mm and dispose away from site as instructed by the Engineer | SM | 21
2.03 | The contractor is reminded that all concrete works must be vibrated using a poker vibrator and all scheduling, dimensioning, bending and cutting of steel reinforcement for concrete to be as per BS 4466
2.04 | Excavate starting from stripped level a 600mm wide foundation trench to a depth not exceeding 0.5m in normal soil | CUM | 6
Fillings
2.05 | Return, fill and ram around foundations | CUM | 3
Mass Concrete
2.06 | Supply all materials and cast a 50mm thick concrete blinding to bed of foundation wall (mix ratio 1:4:8) | SM | 12
2.07 | Supply and fix steel bars in foundation trench concrete work including cutting, bending, hoisting, and tying wire and supporting all in position, D12 @ 200 c/c | KG | 85
Reinforced concrete
2.08 | Supply all materials and cast a 150mm thick vibrated reinforced foundation concrete 1:2:4 (concrete class 20/20) | CUM | 1
Rough natural stone with crushing strength 12Kn
2.09 | Supply and build, 200mm thick stone foundation walling in cement and sand mortar (1:3). Reinforce with and including 20swg x 25mm wide hoop iron in every alternative course; height 1.2m. | SM | 30
2.1 | 300mm thick approved hard-core,well compacted in layers not exceeding 150mm and blinded using 50mm marram/quarry dust | SM | 13
2.11 | Rough formwork to sides of slab | SM | 12
2.12 | Supply and fix steel bars in slab concrete work including cutting, bending, hoisting, and tying wire and supporting all in position, D8 @ 200 c/c | KG | 100
2.13 | Supply all materials and cast a 175mm vibrated reinforced concrete slab mix1:2:4 or class 20/20 | CUM | 2.2
2.14 | 15mm thick two coat cement sand (1:3) plaster trowelled smooth and comprising 12mm backing and 3mm finishing coat the columns. | SM | 40
Supply, handle, deliver to site, lay and joint the following
2.15 | 1 1/2" GI pipe | NO | 1
2.16 | 1 1/2" GI elbow | NO | 4
2.17 | 1" dia Gate valve | NO | 3
2.18 | 1" GI union | NO | 3
2.19 | 1" hexagonal GI nipple | NO | 2
2.2 | 1" long threaded GI nipple | NO | 3
2.21 | 1" backnuts | NO | 6
Sub-Total
3 | 2 no. standpipes
3.01 | Supply and lay 40mm HDPE pipe PN12.5 | M | 100
3.02 | 40mm HDPE male Adaptor | NO | 3
3.03 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 100m) from tank to water point | M | 100
3.04 | Erect a stand pipe at the strategic location as directed by Engineer Note: The stand pipe will consist of 1" GS stand pipe, ¾" pegler taps(2No.), 1" pegler Gate Valve, 1" union, 1x¾" R. Bush, 1" GI elbows (2No.) The cost to include concrete for stand pipe support and slab | NO | 1
Soak Away Pit
3.05 | Bulk excavations 2m diameter x 3.0m depth hole | CUM | 10
3.06 | Hardcore filling to 2.7m depth | CUM | 8
3.07 | Supply and lay 500 gauge polythene damp proof membrane over the hardcore surface | SM | 4
3.08 | 300mm thick normal soil backfilled in 2 layers of 150mm each and well compacted | SM | 4
3.09 | Construct 450x450x300mm deep silt trap including supply and installation of manhole cover | No. | 1
3.1 | Supply and fix 4" dia gully trap | NO | 1
3.11 | Supply and fix 4" dia waste pipe | M | 3
3.12 | Supply and fix 4" dia Swept Bend With Inspection | NO | 2
Sub-Total for 2 Stand Pipes
GRAND SUMMARY PAGE
1 | Preliminary and General items
2 | Repair/Construction of Tank Platform (2.5mx5m)
3 | 2 no. standpipes
TOTAL
Add 10% for Contingencies
GRAND TOTAL
REHABILITATION AND IMPROVEMENT OF WATER SUPPLY AT NANG'OLEMARET PRIMARY
ITEM | DESCRIPTION | Unit | Qty | Rate (KSH) | Amnt (Ksh) Inclusive of VAT and Other duties
1 | Preliminary and general items
1.01 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
Total
2 | Elevated Tank Tower (3m high) and 5CM tank
2.01 | Pipe trench: Excavate and backfill for pipe trench (0.4m x 0.4m x 330m) from Borehole to School Proposed School Tank | CM | 19.5
2.01 | Clear site of all shrubs and small trees not exceeding 600mm girth and cart away or burn arisings. | M2 | 10.2
2.02 | Excavate for foundation column bases not exceeding 1.5m deep commencing from reduced level. | M3 | 6
2.03 | Extra -over excavation in any position for excavation in rock | M3 | 1.2
50 mm plain concrete (1:4:8)-class 15/20 mm))blinding to:
2.04 | Column bases | M2 | 5.8
Graduated strengthvibrated reinforced concrete class 25 aggregate in ;-
2.05 | Column bases | M3 | 1.8
2.06 | Foundation columns | M3 | 0.9
Reinforcement (all provisional)
High yield deformed steel bar reinforcement to KS ISO 6935-2, grade B500B
2.07 | 12mm diamater bars | Kg | 150
2.08 | 8mm diamater bars | Kg | 24
Sawn formwork to:
2.09 | Vertical sides of column bases (8"x1" & 6"x1") | M2 | 5.8
2.1 | Ditto but to vertical sides of column (8"x1" & 6"x1") | M2 | 8
Mild steel
2.11 | Cut mortice 225mm deep in reinforced concrete column for and including embedding 12mm diameter bolt & nuts with concrete (1:2:4) and make good | No | 16
2.12 | 350x350x10mm steel plate | No | 4
RSA Bracings
2.13 | 75x50x6mm | M | 8
2.14 | 50x50x6mm | M | 6
2.15 | 100x100x6mm | M | 2.4
Superstructures (Steel Frame Works)
Steel Columns
2.13 | 4 NO. 100mm x 100mm x 6mm x 5000mm long SHS mild steel frame top end with welded square - holder butt for 75 x 75mm plate to connect with horizontal steel members above | M | 20
2.14 | 50mm x 50mm x 6mm RSA bracings bolted to the columns | M | 55
2.15 | 75mm x 50mm x 6mm SHS horizontal tubes welded to ends of the steel columns | M | 8
Platform
2.16 | 100mm x 100mm x 4mm SHS mild steel frame support beams | M | 18
2.17 | Provide and supply aluminum diamond plate - brigt finish 3003 H22 | M2 | 8
2.18 | Supply and weld 32mm x 2mm CHS for guard rails | M | 24
Prepare and apply three coats of gloss paint to:-
2.19 | Metal surface girth not exceeding 100mm | M2 | 20
2.2 | Supply and install a plastic water storage tank 5m³ Kentainer type or equivalent to be approved by engineer, drilled with inlet(40mm), outlet(40mm) and overflow(40mm) holes and necessary flanges fittings | No | 1
Supply, handle, deliver to site, lay and joint the following
2.21 | 63 x 50mm HDPE R. Coupling | NO | 1
2.22 | 50mm HDPE male Adaptor | NO | 2
2.23 | 1 1/2" GI pipe | NO | 2
2.24 | 1 1/2" GI elbow | NO | 4
2.25 | 1 1/2" dia Gate valve | NO | 3
2.26 | 1 1/2" GI union | NO | 3
2.27 | 1 1/2" hexagonal GI nipple | NO | 5
2.28 | 1 1/2" 4000mm long threaded GI pipe | NO | 1
2.29 | 1 1/2" long threaded GI nipple | NO | 2
2.3 | 1 1/2" backnuts | NO | 6
Sub-Total
3 | Construction of 130m supply pipeline to 10CM Tank
Earthworks
3.01 | Excavate trench for Pipes minimum depth of 1000mm and backfill as directed by the Engineer. | M | 130
Pipework
Provide in the trench the following pipes and fittings;-
3.02 | 40mm diameter PN12 HDPE pipe;-as diretced by the Engineer | M | 130
3.03 | 40mm diameter PN16 HDPE coupling | No. | 2
3.03 | 63 x 40mm HDPE R. Tee | NO | 1
3.04 | 40mm HDPE male Adaptor | NO | 2
3.05 | 1 1/4" GI pipe | NO | 2
3.06 | 1 1/4" GI elbow | NO | 4
3.07 | 1 1/4" dia Gate valve | NO | 3
3.08 | 1 1/4" GI union | NO | 3
3.09 | 1 1/4" hexagonal GI nipple | NO | 5
3.1 | 1 1/4" 4000mm long threaded GI pipe | NO | 1
3.11 | 1 1/4" long threaded GI nipple | NO | 2
3.12 | 1 1/4" backnuts | NO | 4
Sub Total
4 | 2 no. standpipes
4.01 | Supply and lay 40mm HDPE pipe PN12.5 | M | 70
4.02 | 40mm HDPE male Adaptor | NO | 3
4.03 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 70m) from tank to water point | M | 80
4.04 | Erect a stand pipe at the strategic location as directed by Engineer Note: The stand pipe will consist of 1" GS stand pipe, ¾" pegler taps(2No.), 1" pegler Gate Valve, 1" union, 1x¾" R. Bush, 1" GI elbows (2No.) The cost to include concrete for stand pipe support and slab | NO | 1
Soak Away Pit
4.05 | Bulk excavations 2m diameter x 3.0m depth hole | CUM | 10
4.06 | Hardcore filling to 2.7m depth | CUM | 8
4.07 | Supply and lay 500 gauge polythene damp proof membrane over the hardcore surface | SM | 4
4.08 | 300mm thick normal soil backfilled in 2 layers of 150mm each and well compacted | SM | 4
4.09 | Construct 450x450x300mm deep silt trap including supply and installation of manhole cover | No. | 1
4.1 | Supply and fix 4" dia gully trap | NO | 1
4.11 | Supply and fix 4" dia waste pipe | M | 3
4.12 | Supply and fix 4" dia Swept Bend With Inspection | NO | 2
Sub-Total for 2 Stand Pipes
GRAND SUMMARY PAGE
1 | Preliminary and general items
2 | Elevated Tank Tower (3m high) and 5CM tank
3 | Construction of 130m supply pipeline to 10CM Tank
4 | 2 no. standpipes
TOTAL
Add 10% for Contingencies
GRAND TOTAL
REHABILITATION AND IMPROVEMENT OF WATER SUPPLY AT TOWOKAYENI PRIMARY
ITEM | DESCRIPTION | Unit | Qty | Rate (KSH) | Amnt (Ksh), Inclusive of VAT and Other duties
1 | Preliminary and general items
1.01 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
Total
2 | Supply of 10CM Tank and connection to reliable pipeline
2.01 | Pipe trench: Excavate and backfill for pipe trench (0.4m x 0.4m x 330m) from Connection to School Proposed School Tank | LM | 400
2.02 | Supply and install a plastic water storage tank 10m³ Kentainer type or equivalent to be approved by engineer, drilled with inlet(40mm), outlet(40mm) and overflow(40mm) holes and necessary flanges fittings | No | 1
Offtake point
2.03 | Installation of a 90 x 40mm tee junction and control valve, cost to include all fittings and manhole | No. | 1
Supply, handle, deliver to site, lay and joint the following
2.03 | Supply and lay 40mm HDPE pipe PN12.5 | M | 400
2.04 | 1 1/4" GI pipe | NO | 1
2.05 | 1 1/4" GI elbow | NO | 4
2.06 | 1 1/4" dia Gate valve | NO | 3
2.07 | 1 1/4" GI union | NO | 3
2.08 | 1 1/4" hexagonal GI nipple | NO | 5
2.09 | 1 1/4" 4000mm long threaded GI pipe | NO | 1
2.1 | 1 1/4" long threaded GI nipple | NO | 2
2.11 | 1 1/4" backnuts | NO | 6
Sub-Total
3 | 2 no. standpipes
3.01 | Supply and lay 40mm HDPE pipe PN12.5 | M | 80
3.02 | 40mm HDPE male Adaptor | NO | 3
3.03 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 80m) from tank to water point | M | 80
3.04 | Erect a stand pipe at the strategic location as directed by Engineer Note: The stand pipe will consist of 1" GS stand pipe, ¾" pegler taps(2No.), 1" pegler Gate Valve, 1" union, 1x¾" R. Bush, 1" GI elbows (2No.) The cost to include concrete for stand pipe support and slab | NO | 1
Soak Away Pit
3.05 | Bulk excavations 2m diameter x 3.0m depth hole | CUM | 10
3.06 | Hardcore filling to 2.7m depth | CUM | 8
3.07 | Supply and lay 500 gauge polythene damp proof membrane over the hardcore surface | SM | 4
3.08 | 300mm thick normal soil backfilled in 2 layers of 150mm each and well compacted | SM | 4
3.09 | Construct 450x450x300mm deep silt trap including supply and installation of manhole cover | No. | 1
3.1 | Supply and fix 4" dia gully trap | NO | 1
3.11 | Supply and fix 4" dia waste pipe | M | 3
3.12 | Supply and fix 4" dia Swept Bend With Inspection | NO | 2
Sub-Total for 2 Stand Pipes
GRAND SUMMARY PAGE
1 | Preliminary and general items
2 | Supply of 10CM Tank and connection to reliable pipeline
3 | 2 no. standpipes
TOTAL
Add 10% for Contingencies
GRAND TOTAL
GRAND SUMMARY
1 | GRAND TOTAL FOR KAKUMA GIRLS PRIMARY
2 | GRAND TOTAL FOR KAMUDEI PRIMARY
3 | GRAND TOTAL FOR NANGOLEMARET PRIMARY
4 | GRAND TOTAL FOR TOWOKAYENI PRIMARY
GRAND TOTAL KES- Inclusive of VAT and Other duties