## CAMP SCHOOL - LOT 7
REFUGEE CAMP SCHOOLS LOT 7- Alnur-Gambella-Loikitaung-Peace
REHABILITATION AND IMPROVEMENT OF WATER SUPPLY AT ALNUR PRIMARY SCHOOL
ITEM | DESCRIPTION | Unit | Qty | Rate (KSH) | Amnt (Ksh) Inclusive of VAT and Other duties
1 | Preliminary and general items
1.01 | Mobilization of materials and personnel 150km from Lodwar Town to sites (Alnur, Gambela, Peace and Lokitaung Primary Schools). Rate shall be inclusive of setting up site and temporary stores, demobilization after completion of works | LS | 1
1.02 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
Total
2 | Rerouting of Pipeline to Elevated Tank
2.01 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 200m) from tank to water point | M | 200
2.02 | Supply and lay 50mm HDPE pipe PN12.5 | M | 200
2.03 | 50mm HDPE male Adaptor | NO | 2
2.04 | 1 1/2" GI elbow | NO | 1
2.05 | 1 1/2" dia Gate valve | NO | 1
2.06 | 1 1/2" GI union | NO | 3
2.07 | 1 1/2" hexagonal GI nipple | NO | 2
Sub-Total
3 | 1 no. standpipe
3.01 | Supply and lay 40mm HDPE pipe PN12.5 | M | 70
3.02 | 40mm HDPE male Adaptor | NO | 3
3.03 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 30m) from tank to water point | M | 70
3.04 | Erect a stand pipe at the strategic location as directed by Engineer Note: The stand pipe will consist of 1" GS stand pipe, ¾" pegler taps(2No.), 1" pegler Gate Valve, 1" union, 1x¾" R. Bush, 1" GI elbows (2No.) The cost to include concrete for stand pipe support and slab | NO | 1
Soak Away Pit
3.05 | Bulk excavations 2m diameter x 3.0m depth hole | CUM | 10
3.06 | Hardcore filling to 2.7m depth | CUM | 8
3.07 | Supply and lay 500 gauge polythene damp proof membrane over the hardcore surface | SM | 4
3.08 | 300mm thick normal soil backfilled in 2 layers of 150mm each and well compacted | SM | 4
3.09 | Construct 450x450x300mm deep silt trap including supply and installation of manhole cover | No. | 1
3.1 | Supply and fix 4" dia gully trap | NO | 1
3.11 | Supply and fix 4" dia waste pipe | M | 3
3.12 | Supply and fix 4" dia Swept Bend With Inspection | NO | 2
Sub-Total
GRAND SUMMARY PAGE
1 | Preliminary and general items
2 | Rerouting of Pipeline to Elevated Tank
3 | 1 no. standpipe
TOTAL
Add 10% for Contingencies
GRAND TOTAL KES- Inclusive of VAT and Other duties
REHABILITATION AND IMPROVEMENT OF WATER SUPPLY AT GAMBELLA PRIMARY SCHOOL
ITEM | DESCRIPTION | Unit | Qty | Rate (KSH) | Amnt (Ksh) Inclusive of VAT and Other duties
1 | Preliminary and general items
1.01 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
Total
2 | Repair of leaking steel tank
2.01 | Prepare surface and apply approved sealant to the 2 leaking points on the bottom panel of the tank | LS | 1
2.02 | Prepare surface and apply aluminium paint to the external surface of the tank | SM | 35
Sub-Total
3 | 2 no. standpipes
3.01 | Supply and lay 40mm HDPE pipe PN12.5 | M | 50
3.02 | 40mm HDPE male Adaptor | NO | 3
3.03 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 50m) from tank to water point | M | 50
3.04 | Erect a stand pipe at the strategic location as directed by Engineer Note: The stand pipe will consist of 1" GS stand pipe, ¾" pegler taps(2No.), 1" pegler Gate Valve, 1" union, 1x¾" R. Bush, 1" GI elbows (2No.) The cost to include concrete for stand pipe support and slab as shown in the drawings | NO | 1
Soak Away Pit
3.05 | Bulk excavations 2m diameter x 3.0m depth hole | CUM | 10
3.06 | Hardcore filling to 2.7m depth | CUM | 8
3.07 | Supply and lay 500 gauge polythene damp proof membrane over the hardcore surface | SM | 4
3.08 | 300mm thick normal soil backfilled in 2 layers of 150mm each and well compacted | SM | 4
3.09 | Construct 450x450x300mm deep silt trap including supply and installation of manhole cover | No. | 1
3.1 | Supply and fix 4" dia gully trap | NO | 1
3.11 | Supply and fix 4" dia waste pipe | M | 3
3.12 | Supply and fix 4" dia Swept Bend With Inspection | NO | 2
Sub-Total for 2 Stand Pipes
GRAND SUMMARY PAGE
1 | Preliminary and general items
2 | Repair of leaking steel tank
3 | 2 no. standpipes
TOTAL
Add 10% for Contingencies
GRAND TOTAL-KES- Inclusive of VAT and Other duties
REHABILITATION AND IMPROVEMENT OF WATER SUPPLY AT LOKITAUNG PRIMARY SCHOOL
ITEM | DESCRIPTION | Unit | Qty | Rate (KSH) | Amnt (Ksh) Inclusive of VAT and Other duties
1 | PRELIMINARY AND GENERAL ITEMS
1.01 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
Total
2 | 400M PIPELINE EXTENSION TO THE SCHOOL
Earthworks
2.01 | Excavate trench for Pipes maximum depth of 1000mm and backfill as directed by the Engineer. | M | 400
Pipework
Provide in the trench the following pipes and fittings;-
2.02 | 63mm diameter PN12 HDPE pipe;-as diretced by the Engineer | M | 150
2.03 | 63mm diameter PN16 HDPE Adapter | No. | 1
2.04 | 4"x2" reducing socket | No. | 1
Offtake point
2.04 | Supply & Installation of a 110 x 63mm HDPE Reducer Tee junction | No. | 1
2.05 | Supply & Installation of a 63mm HDPE Adapter | No. | 2
2.06 | Supply & Installation of a 2" Gate Valve (peglar type) | No. | 1
2.07 | Supply & Installation of a 2" Hex Nipple | No. | 1
2.08 | Supply & Installation of a 2" union | No. | 1
2.07 | Construct 800x800x1000mm deep inspection chabmer with lockable ms cover | No. | 1
Sub Total
3 | 2 HANDWASHING POINTS
3.01 | Pipe trench: Excavate for pipe trench (0.4m x 0.4m x 60m) from tank to water point | M | 60
3.02 | Excavation to level foundation base to receive hardcore filling | CM | 3.5
3.03 | Provide Place and compact approved hardcore to the thickness shown in the drawing.and ram to attain even level | SM | 11
3.04 | Blinding Concrete, 50 mm thick Class 15/20 to base of the Tapstand | SM | 11
3.05 | Formwork for platform | SM | 3
3.06 | Reinforced Concrete Class 20/20 to the floor Slab as directed by Engineer at site | CM | 1.2
3.07 | Provide BRC mesh class A142 to be placed at the floor slab as directed by Engineer at site | SM | 8
3.08 | 225 mm thick | SM | 1.2
Plastering
3.09 | Plaster; 25mm with cement, Water proofing and sand mortar 1:1:3 mix on vertical faces of the tapstand | SM | 3
Pipes and Fittings
3.1 | Supply and lay 40mm HDPE pipe PN12.5 | M | 60
3.11 | 40mm HDPE male Adaptor | NO | 3
3.12 | 1 1/4" GI pipe | NO | 1
3.13 | 1 1/4" x 1" Reducing GI Socket | NO | 1
3.14 | 1" GI Pipe Threaded both sides of length 2m | NO | 1
3.15 | 1" GI Pipe Threaded both sides of length 1m | NO | 1
3.16 | 1" GI Pipe Threaded both sides of length 400mm | NO | 2
3.17 | 1" dia GI elbows | NO | 2
3.18 | 1" dia equal GI tee | NO | 2
3.19 | 1" dia cross GI tee | NO | 1
3.2 | 1" dia Long Nipples | NO | 7
3.21 | 1" dia Hex Nipples | NO | 2
3.22 | 1/2" dia Hex Nipples | NO | 14
3.22 | 1" dia GI sockets | NO | 2
3.23 | 1" dia Union | NO | 1
3.24 | 1" dia peglar taps | NO | 6
3.25 | 1/2" dia peglar taps | NO | 14
Soak Away Pit
3.25 | Bulk excavations 2m diameter x 3.0m depth hole | CUM | 10
3.26 | Hardcore filling to 2.7m depth | CUM | 8
3.27 | Supply and lay 500 gauge polythene damp proof membrane over the hardcore surface | SM | 4
3.28 | 300mm thick normal soil backfilled in 2 layers of 150mm each and well compacted | SM | 4
3.29 | Construct 450x450x300mm deep silt trap including supply and installation of manhole cover | No. | 1
3.3 | Supply and fix 4" dia gully trap | NO | 1
3.31 | Supply and fix 4" dia waste pipe | M | 3
3.32 | Supply and fix 4" dia Swept Bend With Inspection | NO | 2
Sub-Total for 2 HWS
GRAND SUMMARY PAGE
1 | PRELIMINARY AND GENERAL ITEMS
2 | 400M PIPELINE EXTENSION TO THE SCHOOL
3 | 2 HANDWASHING POINTS
TOTAL
Add 10% for Contingencies
GRAND TOTAL KES- Inclusive of VAT and Other duties
REHABILITATION AND IMPROVEMENT OF WATER SUPPLY AT PEACE PRIMARY SCHOOL
ITEM | DESCRIPTION | Unit | Qty | Rate (KSH) | Amnt (Ksh) Inclusive of VAT and Other duties
1 | Preliminary and general items
1.01 | Fabricate a sign post with a display area of 1350mm x900mm and a support frame of 1500mm above ground level and concreted (grade 20) on the ground 300mm below the ground level. The sign post should be primed and painted with three coats of high grade gloss paint and written as per the engineer’s instruction. Material shall be mild steel gauge 16 and board printed on both sides. | No | 1
Sub-Total
2 | Supply of 10CM Tank and installation at existing Tank Platform
Supply, handle, deliver to site, lay and joint the following
2.01 | Supply and install a plastic water storage tank 10m³ Kentainer type or equivalent to be approved by engineer, drilled with inlet(40mm), outlet(40mm) and overflow(40mm) holes and necessary flanges fittings | No | 1
2.02 | 1 1/4" GI pipe | NO | 1
2.03 | 1 1/4" GI elbow | NO | 4
2.03 | 1 1/4" X 1" dia Reducing Socket | NO | 1
2.04 | 1" dia Gate valve | NO | 2
2.05 | 1" GI union | NO | 2
2.06 | 1" hexagonal GI nipple | NO | 2
2.07 | 1" long threaded GI nipple | NO | 2
2.08 | 1" backnuts | NO | 4
Sub-Total
3 | Pipeline inspection and rehabilitation
Supply, handle, deliver to site, lay and joint the following
3.01 | Provisional sum of Kes. 100,000 for operationalization and rehabilitation of existing distribution network | LS | 1
Sub-Total
GRAND SUMMARY PAGE
1 | Preliminary and general items
2 | Supply of 10CM Tank and installation at existing Tank Platform
3 | Pipeline inspection and rehabilitation
TOTAL
Add 10% for Contingencies
GRAND TOTAL
GRAND SUMMARY
1 | GRAND TOTAL FOR ALNUR PRIMARY
2 | GRAND TOTAL FOR GAMBELLA PRIMARY
3 | GRAND TOTAL FOR LOKITAUNG PRIMARY
4 | GRAND TOTAL FOR PEACE PRIMARY
GRAND TOTAL KES-Inclusive of VAT and Other duties