Technical report summary

| Client | International Rescue Committee (IRC) |
| --- | --- |
| Facility | IRC Hagadera Health Facility — Hagadera, Dadaab, Garissa County, Kenya |
| Project Scope | 107 kWp Ground-Mount Solar PV + 184.32 kWh BESS + Full Electrical Distribution Rehabilitation |
| Site Visit | Mandatory before submission — refer to Section 9 |
| Technical Report Date | April 2026 |

NOTE

Bidders must conduct their own independent site visit before submitting a tender. The information in this document is based on the April 2026 technical assessment and is provided to assist bidders in understanding the scope. It does not replace a full independent assessment.

1. Facility Description

IRC Hagadera Health Facility is a humanitarian healthcare facility operated by the International Rescue Committee (IRC) in Hagadera, within the Dadaab refugee camp complex, Garissa County, Kenya. The facility provides primary and secondary healthcare services to the refugee and host community population.

The site is fully off-grid with no Kenya Power connection, relying entirely on its solar-battery hybrid system and diesel generator backup for all power needs. The facility compound includes multiple ward buildings, a hospital kitchen, drug store, and associated support structures. Critical clinical loads including cold chain refrigeration, overnight wards, and emergency lighting run continuously through the night, making uninterrupted power supply essential to patient safety.

| Location | Hagadera, Dadaab, Garissa County, Kenya (0.06°N, 40.43°E) |
| --- | --- |
| Facility Type | Off-grid hospital / health centre — 24/7 operation |
| Grid Connection | None — fully off-grid. No Kenya Power connection |
| Compound | Multiple ward buildings, hospital kitchen, drug store, generator shelter and support structures |
| Solar Resource (GHI) | 6.2 kWh/m²/day (NASA POWER data for Dadaab) |
| Fuel | Diesel — delivered to site (USD 1.20/litre) |
| Existing System | 90.1 kWp mixed PV array (178 panels), Deye SUN-80K hybrid inverter (80 kW), 36× Dyness S51100 LiFePO4 (184.32 kWh), Sutech WP-100GF generator (100 kVA) |

2. Electrical Load Profile

A comprehensive electrical load survey was conducted across all departments of IRC Hagadera Health Facility, covering 59 equipment categories and 1,285 individual units. A full 24-hour metered load profile was recorded to establish the actual energy demand pattern. All figures below are the basis for system sizing and must be used by all bidders.

| Daily Energy Demand | 591.5 kWh/day |
| --- | --- |
| Measured Daily Average Load | 24.65 kW |

| Night Base Load (00:00–06:00) | 8.238 kW — cold chain, oxygen concentrator, base clinical systems |
| --- | --- |
| Measured Peak Load | 54.239 kW at 11:00 on survey day |
| Design Peak Band | 67–70 kW (stated design peak — not reached on survey day) |
| HVAC Daily Energy | 248 kWh/day — dominant load category (42% of total) |
| Clinical Daily Energy | 166 kWh/day (28% of total) |
| Cold Chain Daily Energy | 83 kWh/day — continuous 24/7 operation |
| General Loads Daily Energy | 41 kWh/day |
| ICT / Admin Daily Energy | 30 kWh/day |
| Lighting Daily Energy | 12 kWh/day |
| Lab Daily Energy | 12 kWh/day |
| Nameplate Installed Capacity | 274.20 kW — sum of all rated equipment across 59 categories, 1,285 units |
| Recommended LPSP | 1% maximum — healthcare facility critical load standard |
| Facility Operating Hours | 24/7 — all clinical departments, cold chain and base systems continuous |

2.1 Operational Period Summary

| Time | Phase | Load (kW) | Active Equipment & Notes |
| --- | --- | --- | --- |
| 00:00– | Night base | ~8.2 kW | Cold chain, oxygen concentrator, base clinical. All non-essential loads off. |
| 06:00 |  |  |  |
| 06:00– | Early morning | ~10–15 | Lighting, fans, water dispensers. First staff arrive. |
| 08:00 |  | kW |  |
| 08:00– | Morning build-up | ~40.6 kW | All AC units start. Full lighting. Clinical equipment powered up. Rapid ramp to operating plateau. |
| 10:00 |  |  |  |
| 10:00– | Operating | 48–54 kW | Full facility operation. HVAC, clinical, lab, general and admin all active. Peak 54.2 kW at 11:00. |
| 14:00 | plateau |  |  |
| 14:00– | Afternoon | 42–48 kW | Sustained clinical activity. All departments active. Slight reduction from noon peak. |
| 16:00 | plateau |  |  |
| 16:00– | Evening wind- | ~37–47 | Gradual reduction as admin and general loads step down. |
| 18:00 | down | kW |  |
| 18:00– | Evening taper | ~13–20 | Reduced clinical activity. Ward and emergency loads sustained. |
| 20:00 |  | kW |  |
| 20:00– | Late night | ~8–14 | Minimal lighting and fans. Emergency and ward loads. Approaching night base. |
| 00:00 |  | kW |  |

2.2 Load Profile Charts

Figure 1 — IRC Hagadera: Measured 24-Hour Load Profile | Avg = 24.65 kW | Peak = 54.24 kW at 11:00  | Design Peak = 67–70 kW | Night Base = 8.238 kW | Daily = 591.5 kWh/day

Figure 2 — Load Duration Curve  | Facility exceeds 40 kW for approximately 8 hours/day (33% of time)

Figure 3 — Estimated Load Composition by Category  | HVAC and Clinical loads dominate the daytime peak period 08:00–16:00

Figure 4 — Daily Energy Consumption by Category (kWh/day) | Total = 591.5 kWh/day

2.3 HOMER Pro Load Profile — 24-Hour Data Table

The table below contains the full 24-hour hourly component breakdown used as input for the HOMER Pro energy simulation. Bidders must use these values for all system sizing calculations.

| Hour | Total (kW) | Base (kW) | HVAC (kW) | Clinical (kW) | Lab (kW) | General (kW) | ICT/Admin (kW) | Lighting (kW) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 00:00 | 8.65 | 8.65 | 0.00 | 0.00 | 0.00 | 0.40 | 0.00 | 0.00 |
| 01:00 | 8.99 | 8.59 | 0.00 | 0.00 | 0.00 | 0.40 | 0.00 | 0.00 |
| 02:00 | 8.51 | 8.51 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| 03:00 | 8.89 | 8.60 | 0.00 | 0.00 | 0.00 | 0.30 | 0.00 | 0.00 |
| 04:00 | 8.87 | 8.57 | 0.00 | 0.00 | 0.00 | 0.30 | 0.00 | 0.00 |
| 05:00 | 8.63 | 8.63 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| 06:00 | 8.24 | 8.24 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 | 0.00 |
| 07:00 | 10.94 | 8.31 | 0.53 | 0.00 | 0.32 | 0.10 | 0.10 | 1.58 |
| 08:00 | 40.63 | 8.81 | 11.75 | 1.00 | 4.41 | 2.45 | 1.47 | 10.74 |
| 09:00 | 48.50 | 9.00 | 16.00 | 1.50 | 5.50 | 2.50 | 1.00 | 13.00 |
| 10:00 | 53.05 | 9.51 | 17.52 | 2.00 | 6.01 | 2.50 | 1.50 | 14.01 |
| 11:00 | 54.24 | 9.51 | 18.01 | 2.50 | 6.50 | 2.50 | 1.20 | 14.02 |
| 12:00 | 51.78 | 9.50 | 16.49 | 1.50 | 6.50 | 2.50 | 1.30 | 14.49 |
| 13:00 | 42.09 | 9.00 | 12.00 | 1.20 | 5.50 | 2.50 | 1.10 | 11.09 |
| 14:00 | 46.17 | 8.99 | 13.99 | 1.50 | 5.50 | 2.50 | 1.70 | 11.99 |
| 15:00 | 47.93 | 9.01 | 15.01 | 1.00 | 5.50 | 2.50 | 1.90 | 14.01 |
| 16:00 | 36.64 | 9.01 | 10.01 | 1.50 | 4.00 | 2.00 | 1.10 | 9.02 |
| 17:00 | 20.86 | 8.48 | 3.49 | 1.00 | 1.50 | 2.00 | 0.90 | 3.49 |
| 18:00 | 13.41 | 8.51 | 1.00 | 1.50 | 0.50 | 1.50 | 0.40 | 0.00 |
| 19:00 | 11.87 | 8.48 | 0.50 | 1.00 | 0.50 | 0.78 | 0.60 | 0.00 |
| 20:00 | 10.42 | 8.28 | 0.00 | 0.49 | 0.29 | 1.50 | 0.29 | 0.00 |
| 21:00 | 13.79 | 8.50 | 0.50 | 2.00 | 0.80 | 0.78 | 0.50 | 0.80 |
| 22:00 | 16.00 | 8.00 | 2.30 | 2.80 | 1.10 | 0.90 | 1.30 | 0.00 |
| DAILY | 591.5 kWh | ~200 kWh | 248 kWh | ~41 kWh | ~12 kWh | ~41 kWh | ~30 kWh | ~12 kWh |

3. Full Equipment Register — IRC Hagadera Health Facility

The register covers all appliance categories identified during the field survey. Bidders must verify all quantities and power ratings during the mandatory site visit. The nameplate installed capacity is 274.20 kW across 59 categories and 1,285 units. Design daily energy of 591.5 kWh/day reflects actual operating patterns with diversity factors and is the basis for all system sizing.

| HVAC — IRC HAGADERA │ Air conditioning & ventilation — dominant daytime category: 248 kWh/day (42% of total) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment | Qty | Power Rating | Hrs/Day | kWh/Day | Notes |
| Split AC Unit (1.5 kW) | est. | 1,500 W | 10 | est. | All wards and clinical areas — dominant peak-hour load |
| Ceiling Fan | est. | 70 W | 10 | est. | All wards, corridors and clinical areas |
| Sub-total HVAC | — | — | — | 248.0 | 42% of 591.5 kWh/day total |

| CLINICAL EQUIPMENT │ Medical & clinical loads — OT, lab, maternity, wards: 166 kWh/day (28% of total) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment | Qty | Power Rating | Hrs/Day | kWh/Day | Notes |
| Oxygen Concentrator | est. | 300 W | 8 | est. | Clinical — some units continuous 24/7 |
| Autoclave / Steriliser | est. | 2,000 W | 4 | est. | OT / sterilization room |
| Suction Machine | est. | 300 W | 6 | est. | Various departments |
| Centrifuge | est. | 500 W | 4 | est. | Laboratory |
| Laboratory Analyser | est. | 200 W | 8 | est. | Laboratory |
| Examination / Procedure Light | est. | 60 W | 8 | est. | All examination rooms |
| Nebulizer / Therapy Device | est. | 150 W | 6 | est. | Ward / outpatient |
| Sub-total Clinical | — | — | — | 166.0 | 28% of 591.5 kWh/day total |

| COLD CHAIN │ Continuous 24/7 — primary night base load driver: 83 kWh/day (14% of total) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment | Qty | Power Rating | Hrs/Day | kWh/Day | Notes |
| Vaccine / Pharmaceutical Refrigerator | est. | 160 W | 24 | est. | Cold chain room — 24/7 continuous |
| Freezer / Deep Freezer | est. | 180 W | 24 | est. | Cold chain room — 24/7 continuous |
| Drug Storage Refrigerator | est. | 150 W | 24 | est. | Drug store — continuous |
| Sub-total Cold Chain | — | — | 24 | 83.0 | 14% of 591.5 kWh/day — sets night base load |

| GENERAL LOADS │ Kitchen, domestic and general service loads: 41 kWh/day (7% of total) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment | Qty | Power Rating | Hrs/Day | kWh/Day | Notes |
| Electric Cooker / Hot Plate | est. | 2,000 W | 4 | est. | Hospital kitchen |
| Water Boiler / Dispenser | est. | 550 W | 8 | est. | Various areas |
| Electric Kettle | est. | 1,100 W | 3 | est. | Staff areas |
| Washing Machine | est. | 500 W | 3 | est. | Hospital laundry |
| Sub-total General | — | — | — | 41.0 | 7% of 591.5 kWh/day |

| ICT / ADMIN │ Office, administrative and communications loads: 30 kWh/day (5% of total) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment | Qty | Power Rating | Hrs/Day | kWh/Day | Notes |
| Desktop Computer | est. | 70 W | 8 | est. | Admin and clinical offices — staffed hours |
| Laptop | est. | 65 W | 6 | est. | Mobile staff |

| Printer | est. | 200 W | 4 | est. | Admin offices |
| --- | --- | --- | --- | --- | --- |
| Internet Cabinet / Switch | est. | 120 W | 24 | est. | ICT — continuous 24/7 — part of night base |
| Router / Modem | est. | 30 W | 24 | est. | ICT — continuous 24/7 |
| UPS / Battery Backup | est. | 120 W | 24 | est. | Continuous |
| TV / Monitor | est. | 60 W | 8 | est. | Waiting areas and wards |
| Sub-total ICT/Admin | — | — | — | 30.0 | 5% of 591.5 kWh/day — internet cabinet contributes to night base |

| LIGHTING │ Internal and external lighting across all clinic areas: 12 kWh/day (2% of total) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Equipment | Qty | Power Rating | Hrs/Day | kWh/Day | Notes |
| LED Tube / Fluorescent Fitting (4ft) | est. | 18 W | 12 | est. | All wards and clinical areas |
| LED Bulb | est. | 9 W | 12 | est. | Offices and corridors |
| Security Floodlight / Compound Light | est. | 50–400 W | 8 | est. | Compound — NOTE: system requires full replacement (see Section 5.1) |
| Emergency Light | est. | 10 W | 24 | est. | All clinical areas — continuous |
| Sub-total Lighting | — | — | — | 12.0 | 2% of 591.5 kWh/day — compound lighting requires full replacement |

| FACILITY GRAND | 1,285 | 274.20 | — | 591.5 | Design daily energy after diversity factors — basis for all system sizing |
| --- | --- | --- | --- | --- | --- |
| TOTAL |  | kW |  | kWh/day |  |

* Nameplate total 274.20 kW before diversity factors. Design daily energy 591.5 kWh/day reflects actual operating patterns. Bidders must confirm all quantities during the mandatory site visit.

4. Existing Power System

The facility has a modern, well-specified solar-battery hybrid power system representing a significant capital investment. However, the electrical distribution infrastructure is in a critically dangerous state. Bidders must understand the two-track nature of this project: (1) immediate life-safety electrical remediation and (2) solar PV system upgrade and expansion.

| Solar PV — Section A | JinKo JKM630N-66HL4M-BDV (N-Type) — 120 panels × 630W = 75.6 kWp — Good; DC overvoltage risk: 30-panel strings produce Voc 1,478V — exceeds 1,000V inverter limit |
| --- | --- |
| Solar PV — Section B | 250 Wp panels — 58 panels × 250W = 14.5 kWp — Good condition; needs cleaning |
| Total PV Array | 178 panels = 90.1 kWp DC — both sections require string reconfiguration to comply with inverter voltage limits |
| Hybrid Inverter | Deye SUN-80K-SG02HP3-EU-EM6 — 80 kW AC / 1,000V DC max — Modern; DC overvoltage risk from current Section A string configuration |
| Battery Storage | Dyness S51100 LiFePO4 — 36 units × 5.12 kWh = 184.32 kWh total / ~165.9 kWh usable — Good; battery room moisture concern |
| Backup Generator | Gaston Power 150KVA |
| ATS | Existing on ground |
| System Monitoring | Solplanet monitoring unit on DC combiner box — full monitoring status to be confirmed on-site |
| Night Autonomy (theory) | ~165.9 kWh usable ÷ 8.238 kW night base = ~20 hours theoretical autonomy (subject to battery room remediation) |

5. Site Observations — Items Requiring Attention

The following critical observations were recorded during the April 2026 site inspection. Bidders must inspect all items during their own site visit, confirm current status, and include all necessary remediation in their tender scope.

5.1 Main Supply Cable Under sizing and Active Overheating — CRITICAL FIRE RISK

| Observation | Main supply cable is 35mm² copper (rated ~76–87A) protected by a 250A MCCB — approximately 3× the cable's safe continuous current capacity |
| --- | --- |
| Current Status | Site engineer confirms cables are actively overheating with partially damaged insulation — immediate fire risk |
| MCCB Will Not Protect | The 250A MCCB will not operate to protect the cable from overheating — the cable is the most significant fire risk on site |
| Required Cable | Minimum 70mm² copper conductor over the full ~250m run — subject to derating calculation based on installation method and ambient temperature |
| Intermediate Feeders | 50mm² copper feeders required at all three main looping distribution boxes |

CRITICAL    Main supply cable is actively overheating and must be replaced as the highest priority remedial action. Include full replacement (minimum 70mm²) in tender scope.

5.2 Post-Fire Damage at Main Distribution Board — CRITICAL

| Observation | Confirmed electrical fire at main distribution board — multiple devices show completely melted plastic housing and fused copper busbar contacts on live panel |
| --- | --- |
| System Integrity | Entire distribution system must be treated as having unknown integrity until formal fault investigation is completed |

CRITICAL    All circuits associated with the fire-damaged board must be inspected before continued operation. Full distribution board replacement is required. Include in tender scope.

| Observation | All 60/80A BS1361 cartridge fuse protection in distribution looping boxes — non-compliant with IEC 60364 / BS 7671 / Kenya Cap 314A |
| --- | --- |
| Required Action | Replace all cartridge fuse protection with properly rated MCCBs — new IP65 weatherproof junction/distribution boards with DIN-rail MCCBs at all looping points |
| What to Check | Identify all looping box locations throughout compound, confirm fuse ratings, assess cable condition at each looping point |

| Observation | All outdoor distribution boards severely deteriorated — severe rust, missing doors, fire damage, vegetation inside, conductors exposed to weather and physical contact |
| --- | --- |
| Risk | Life-critical loads (Hospital Kitchen, Drug Store) served by boards fully open to weather — rain creates electrocution and fire risk |
| Required Action | All existing distribution boards beyond repair — full replacement with new IP65-rated weatherproof enclosures |
| What to Check | Inspect all outdoor boards, identify circuits served, confirm replacement board locations and enclosure sizes |

5.3 Cartridge Fuse Protection Throughout Distribution — Critical

5.4 Distribution Boards Severely Deteriorated — High

6. Indicative Proposed System Sizes

The following proposed system sizes are based on the load assessment and HOMER Pro energy simulation results. HOMER Pro winning architecture: 197 kWp PV + 332 kWh LI Battery + 160 kW Converter. The sizing below represents a practical implementation using the existing battery bank. Bidders must verify all sizing against their own site findings and state any variations with justification.

6.1 New Solar PV Array — 107 kWp Ground Mount

| DC System Capacity | 107 kWp |
| --- | --- |
| Module Type | 630 Wp Monocrystalline PERC, 144-cell, efficiency ≥21.3%, Voc ≥49.5V, IP68, IEC61215/61730 certified |
| Module Quantity | 170 modules |
| String Configuration | ~14 strings of 12 modules — DC Voc = 591.4V / Vmp = 492.2V — fully within 1,000V inverter limit (compliant) |
| Array Ground Area | Approximately 540 m² |
| Mounting Structure | Fixed-tilt ground mount — 15°–25° tilt — wind rated 150 km/h — hot-dip galvanised steel |
| Estimated Annual Yield | ~160,500 kWh/year (1,500 equivalent full-load hours at 6.2 kWh/m²/day GHI) |
| DC/AC Ratio | ~1.34 — appropriate for off-grid hybrid application |
| Sizing Basis | 591.5 kWh/day ÷ 6.2 GHI ÷ 0.80 system efficiency = ~119 kWp minimum; 107 kWp new + 90.1 kWp existing = 197.1 kWp combined |

6.2 Inverter — New Deye SUN-80K-SG01HP3

| Proposed Model | Deye SUN-80K-SG01HP3 |
| --- | --- |
| AC Rated Power | 80 kW — 3-phase, 400V / 50 Hz |
| MPPT Channels | 12 MPPT |
| Max DC Input Voltage | 1,000 V DC |
| Battery Communication | CAN / RS485 / Wi-Fi |
| Protection Rating | IP65 |
| Existing Inverter | Deye SUN-80K-SG02HP3-EU-EM6 — retain subject to string reconfiguration and site assessment |
| Sizing Basis | ~1.19× design peak (67 kW × 1.19 = ~80 kW) |

6.3 Battery Energy Storage System — Retain Existing 184.32 kWh

| Existing BESS | 36 × Dyness S51100 LiFePO4 = 184.32 kWh total / ~165.9 kWh usable (90% DoD) |
| --- | --- |
| Battery Chemistry | LiFePO4 — cycle life > 4,000 cycles at 80% capacity retention — round-trip efficiency ≥95% |
| Night Duty Analysis | 8.238 kW × 6 hrs (00:00–06:00) = ~49.4 kWh minimum required — existing 165.9 kWh usable provides ~3.4× margin |
| BESS Condition | Good — modern units; battery room moisture remediation required immediately before recommissioning |
| Battery Room Remediation | Seal all penetrations, improve ventilation, replace combustible backboard — required before system commissioning |
| Sizing Basis | HOMER recommends 332 kWh; existing 184.32 kWh (165.9 kWh usable) provides adequate night coverage — expand if budget permits |
| What to Check on Site | Inspect all 36 modules, confirm BMS LED status, SOC readings, CAN/RS485 comms with inverter, battery room moisture status |

6.4 Backup Generator — Retain with Servicing and ATS

| Existing Generator | Gaston power — 150 kVA / Perkins engine |
| --- | --- |
| Design Peak to Cover | 120kW — within existing 150 kVA generator capacity |
| ATS | present |

7. Summary Scope of Works

All items below must be covered in the tender. Bidders may propose phasing or sequencing, but all items must be included and priced. Life-safety items in Section 7.1 must be actioned immediately — independent of and concurrent with the solar upgrade procurement timeline.

7.1 Safety — Immediate Actions (Independent of Solar Upgrade Timeline)

•    Supply and install water tight power distribution boards complete with protective circuit breakers as stipulated the  BoQ.

•    Replace main supply cable: Replace 35mm² main supply cable with minimum 70mm² copper conductor over the full

~250m run — cables actively overheating with damaged insulation — highest fire risk item on site

7.2 Solar PV System

•    New 107 kWp ground-mount array: 170 × 630 Wp monocrystalline PERC modules on fixed-tilt ground mount —

approximately 540 m² ground area required — wind rated 150 km/h — hot-dip galvanized steel

•	New hybrid inverter: Supply and install 1 × Deye SUN-80K-SG01HP3 80 kW 3-phase hybrid inverter — commission with BMS communication to existing Dyness battery bank

7.3 Electrical Distribution System Rehabilitation

Full supply  and installation of electrical items for electrical distribution and cable upgrade rehabilitation as per shared BoQ.

7.4 Earthing and Lightning Protection

•	Earth rod replacement: Replace corroded earth rod, clamp and termination cable — new 16mm diameter × 2.4m copper-bonded steel rod — add Ground Enhancement Material (GEM) — target R < 1 Ω

•	Lightning protection system: Full LPS assessment per IEC 62305 — design and install LPS — no LPS currently installed — high-value inverter, battery and clinical equipment at risk

•    Re-test and document: Re-test all earth resistance values after works — document and submit with as-built drawings

7.5 Monitoring and Documentation

•	Plant monitoring: Plant-level monitoring system — SCADA/DAS, web dashboard, 5-year license, remote access and alarm capability

•    As-built drawings: CAD drawings, single-line diagrams, O&M manual and test reports — submitted on completion

•	Operator training: On-site training — minimum 2 days covering O&M procedures, safety protocols and emergency response

- Integration – Integrate the new 80kw system with the existing 80Kw system via means of inverter communication         protocols

•	Annual maintenance Year 1: Minimum 3 site visits/year — panel cleaning, thermal scan, performance report, distribution board inspection

8. System Sizing Rationale

The table below compares the current system against the proposed upgrade. All figures are based on 591.5 kWh/day demand and 67–70 kW design peak.

| Component | Current System | Proposed Upgrade | Sizing Basis |
| --- | --- | --- | --- |
|  | 90.1 kWp (178 panels) — good condition; Section A strings over- voltage (Voc 1,478V > 1,000V limit) | 107 kWp new ground mount + retain existing 90.1 kWp = 197.1 kWp combined | 591.5 kWh/day ÷ 6.2 GHI ÷ 0.80 = |
| Solar PV |  |  | ~119 kWp min; HOMER suggests |
| Array |  |  | 197 kWp — new 107 kWp brings system to target |
| Inverter | Deye SUN-80K (80 kW) — modern; DC overvoltage risk from current string config | New Deye SUN-80K-SG01HP3 (80 kW) + retain existing Deye SUN-80K | ~1.19× design peak (67 kW × 1.19 ≈ 80 kW) |
|  | 184.32 kWh / 165.9 kWh usable | Retain existing 184.32 kWh — remediate battery room | 8.238 kW × 6 hrs = ~49 kWh min — |
| Battery Storage |  |  |  |
| Distribution | CRITICAL: fire damage, undersized cables, cartridge fuses, power distribution boards | Full distribution rehabilitation — new MDB, cables, MCCBs | Life-safety compliance — IEC 60364 / BS 7671 / Kenya Electrical Wiring Regs Cap 314A |

9. Mandatory Site Visit

A site visit is mandatory before submission. No tender will be considered from a bidder who has not visited the site. A qualified electrical engineer or technician must be part of the visiting team given the critical electrical distribution deficiencies identified. Allow a full day for a thorough site walkthrough.