## BOQ
BILL OF QUANTITIES – 107 kWp GROUND-MOUNT SOLAR PV & 184.32 kWh BESS
1 × Deye SUN-80K-SG01HP3 (80 kW) Hybrid Inverter ¦ LiFePO4 Battery Storage ¦ Ground Mount Structure ¦ Hangadera
# | Item | Ref. | Description | Specification | Qty | Unit | Unit Price (KSh) | Total Price (KSh)Inclusive of VAT
SECTION A – SOLAR PV MODULES
1 | A1 | PV-01 | Monocrystalline Solar PV Module | 630 Wp, Mono PERC, 144-cell, Voc≥49.5V, efficiency≥21.3%, IP68, IEC61215/61730 certified | 170 | No.
Sub-Total – SOLAR PV MODULES
SECTION B – INVERTERS
Supply and fix Deye SUN-80K-SG01HP3 Hybrid Inverter including inverter wall,AC disconnect inluding inverter programming(Factory settings, grid code configuration, monitoring setup per unit)
3 | B1 | INV-01 | Deye SUN-80K-SG01HP3 Hybrid Inverter | 80 kW, 3-phase, MPPT×12, DC input 1000V, AC output 400V/50Hz, RS485/CAN/WiFi, IP65 | 1 | No.
4 | B2 | INV-02 | Inverter Wall/Frame Mounting Brackets | Hot-dip galvanised steel, rated for 80 kW unit | 1 | Set
5 | B3 | INV-03 | Inverter AC Disconnect / AC Breaker | 3-phase MCB/MCCB 200A, 400V, coordinated protection | 1 | Lot
Sub-Total – INVERTERS
SECTION C – BATTERY ENERGY STORAGE SYSTEM (184.32 kWh)
Supply and install lithium LiFe PO4 battery (including BMS,battery disconnect,enclosure and cabling) including Mechanical fixing, electrical termination, BMS-inverter integration, test
7 | C1 | BAT-01 | LiFePO4 Battery Cabinet | 5.12 kWh / 100Ah modules, stackable rack, BMS integrated | 36 | No.
8 | C2 | BAT-02 | Battery Management System (BMS) – Master/Rack | Master BMS, CAN/RS485 comms, SOC/SOH monitoring, over-voltage/temperature protection | 1 | No.
9 | C3 | BAT-03 | DC Battery Disconnect Switch | 1000V DC, 400A rated, lockable isolator | 1 | No.
10 | C4 | BAT-04 | Battery Enclosure / Cabinet | IP55 rated steel enclosure, ventilated, lockable, painted RAL7035 | 3 | No.
11 | C5 | BAT-05 | Battery Cabling & Interconnects | 95mm² double-insulated DC cable, lugs, cable ties, labels | 1 | Lot
Sub-Total – BATTERY ENERGY STORAGE SYSTEM (148 kWh)
SECTION D – GROUND MOUNT STRUCTURE
Supply and fix ground mounting structure 15°–25° tilt, suitable for 630 Wp modules, wind 150 km/h rated including foundation support including Erection, levelling, torque check, QA inspection
13 | D1 | STR-01 | Fixed-Tilt Ground Mount Structure | Mounting struchure 15°–25° tilt, suitable for 630 Wp modules, wind 150 km/h rated | 107 | Module
14 | D2 | STR-02 | Ground Anchor / Pad Foundation | Driven steel pile or concrete footing per structural design, supply & install | 107 | No.
15 | D3 | STR-03 | Structural Engineering Design | PE-stamped structural designs and drawings for ground mounting structures foundation | 1 | Lot
Sub-Total – GROUND MOUNT STRUCTURE
SECTION E – DC WIRING & STRING COMBINER
17 | E1 | DC-01 | PV Array DC Cable – 6 mm² (Red/Black) | TUV/UL certified, double-insulated, UV resistant, 1000V rated | 1700 | m | 168
18 | E2 | DC-02 | MC4 Connectors (Pair) | TUV certified MC4 male/female, IP68 | 30 | Pair
19 | E3 | DC-03 | String Combiner Box (12-string input) | 12-in / 1-out, 15A string fuse per input, surge protection SPD, IP65 | 1 | No.
20 | E5 | DC-05 | DC Surge Protection Device (SPD) | Type II SPD, 1000V DC, 40kA, DIN rail, per combiner box | 1 | No.
21 | E6 | DC-06 | DC Cable Tray / Conduit | Galvanised perforated cable tray 100×50 mm, with cover, fixings | 100 | m
Sub-Total – DC WIRING & STRING COMBINER
SECTION F – AC WIRING & PROTECTION
Supply and fix the following wiring protection
22 | F1 | AC-02 | AC Output Cable – 3×120 mm² + 70 mm² N/E | XLPE armoured, 3-phase, rated 250A, inverter to MDB | 40 | m
23 | F2 | AC-06 | Earthing & Lightning Protection | Earth rod, bare copper tape, bonding conductors, surge arresters | 1 | Lot
24 | F3 | AC-07 | Cable Labelling, Markers & Ferrules | Heat-shrink labels, cable tags, busbar markers | 1 | Lot
Sub-Total – AC WIRING & PROTECTION
SECTION G – MONITORING & COMMUNICATIONS
25 | G1 | MON-01 | Plant-Level Monitoring System | SCADA/DAS, web dashboard, 5-year licence, remote access, alarms | 1 | No.
Sub-Total – MONITORING & COMMUNICATIONS
SECTION H – CIVIL & INSTALLATION WORKS
26 | H1 | CIV-01 | Site Clearing & Grading | Vegetation removal, levelling of array area (~540 m²) | 1 | Lot
27 | H2 | CIV-06 | Signage & Safety Labelling | DC/AC danger signs, first responder info, arc-flash labels | 1 | Lot
Sub-Total – CIVIL & INSTALLATION WORKS
SECTION I – INSTALLATION,TESTING, COMMISSIONING & DOCUMENTATION
Provide a lumpsum rate for system testing, commisioning-including staff training ,documentation and warranty
28 | I1 | COM-01 | System istallation,testing, Integration & Commissioning | Full system energisation, functional tests, grid code verification, PV string tests CAD drawings, single-line diagrams, O&M manual, test reports, staff training and system integration to existing system | 1 | Lot
Sub-Total – TESTING, COMMISSIONING & DOCUMENTATION
SECTION J – SPARES, WARRANTY & O&M
32 | J1 | SPR-01 | Module Spare Stock (1% of array) | 2 × spare 630 Wp modules for warranty replacements | 2 | No.
33 | J2 | SPR-02 | MC4 Connector Spare Kit | 10 × MC4 pairs, spare fuses, cable end lugs | 1 | Kit
34 | J3 | OM-01 | Annual Preventive Maintenance Contract (Yr 1) | 3× site visits/year, cleaning, thermal scan, report | 1 | Year
Sub-Total – SPARES, WARRANTY & O&M
SECTION K-TRANSPORTATION
| A2 | PV-02 | Materials Transportation & Handling | Delivery to site and unloading | 1 | Lot
Sub-Total – Transportation
PROJECT COST SUMMARY
CONSTRUCTIONS SUB-TOTAL (Sections A–J)
GRAND TOTAL-Inclusive of VAT/other relevant duties
Indicate Warranty period here….................................................................................

## System Summary
SYSTEM TECHNICAL SUMMARY – HANGADERA
PV ARRAY
DC System Capacity | 107 kWp
Module Type | Mono PERC 630 Wp
Module Quantity | 170 modules
No. of Strings | ~14 strings (12 modules each)
Array Tilt Angle | 15°–25° (site-dependent)
Estimated Annual Yield | ~160,500 kWh/year (1,500 h eq.)
INVERTER SYSTEM
Inverter Model | Deye SUN-80K-SG01HP3
Inverter Quantity | 1 unit
Total AC Capacity | 80 kW
DC/AC Ratio | ~1.34
AC Output Voltage | 400 V / 3-phase / 50 Hz
MPPT Channels per Unit | 12 MPPT
BATTERY STORAGE
Total Energy Capacity | 184.32 kWh
Battery Chemistry | LiFePO4 (Lithium Iron Phosphate)
Usable Capacity (90% DoD) | ~133 kWh
Cycle Life (80% capacity) | >4,000 cycles
Round-Trip Efficiency | ≥95%
System Voltage | 48 V (scalable)
BMS | Integrated per rack + master BMS
GRID CONNECTION
Connection Type | 3-phase grid-tied with battery backup
Protection | Anti-islanding, OVR/UVR, OFR/UFR